## i3lite
Domintell
TEST1
setup: | i3lite on iPad4, Connected with Domintell nature software to check, all versions are latest
nature | module | test | remarks
Status |  | NO | on-line token: can't find it
Relay | dbir01 | OK
dimmer | ddim01 | OK
shutter | dtrv01 | NO | scanner imports only 3 shutter channels while there is 4 channels on module no connection possible, no feedback
button | dpbeco01 | SOME | The button on i3lite receives feedback, but doesn't send command
|  | NO | feedback LED: can not be controlled, does not give feedback on state of actual LED
| dnipb06 | SOME | The button on i3lite receives feedback, but doesn't send command
|  | NO | feedback LED: can not be controlled, does not give feedback on state of actual LED
FAN | dmv01 | NO | no controlling nor feedback
input | dism20 | NO | the module has wrong type of connection. It doesn't act as a button
dmx | ddmx01 | NO | not implemented in i3lite
temperature | dtem01 | NO | no response, no feedback, does nothing so far
TEST2
setup: | i3lite on Windows PC, Connected with Domintell nature software to check, all versions are latest
Relay | dbir01 | OK
dimmer | ddim01 | OK
shutter | dtrv01 | NO | scanner imports only 3 shutter channels while there is 4 channels on module no connection possible, no feedback
button | dpbeco01 | SOME | The button on i3lite receives feedback, but doesn't send command
|  | NO | feedback LED: can not be controlled, does not give feedback on state of actual LED
| dnipb06 | SOME | The button on i3lite receives feedback, but doesn't send command
|  | NO | feedback LED: can not be controlled, does not give feedback on state of actual LED
FAN | dmv01 | NO | no controlling nor feedback
input | dism20 | NO | the module has wrong type of connection. It doesn't act as a button
dmx | ddmx01 | NO | not implemented in i3lite
temperature | dtem01 | NO | no response, no feedback, does nothing so far
TEST3
setup: | i3lite on android phone, Connected with Domintell nature software to check, all versions are latest
Relay | dbir01 | SOME | only feedback works, no command could be send
dimmer | ddim01 | OK
shutter | dtrv01 | NO | scanner imports only 3 shutter channels while there is 4 channels on module no connection possible, no feedback
button | dpbeco01 | SOME | The button on i3lite receives feedback, but doesn't send command
|  | NO | feedback LED: can not be controlled, does not give feedback on state of actual LED
| dnipb06 | SOME | The button on i3lite receives feedback, but doesn't send command
|  | NO | feedback LED: can not be controlled, does not give feedback on state of actual LED
FAN | dmv01 | NO | no controlling nor feedback
input | dism20 | NO | the module has wrong type of connection. It doesn't act as a button
dmx | ddmx01 | NO | not implemented in i3lite
temperature | dtem01 | NO | no response, no feedback, does nothing so far

## i3PRO
DTRV workaround
change channels!!
| to control channel | 1 |  | send to channel | 1
| to control channel | 2 |  | send to channel | 3
| to control channel | 3 |  | send to channel | 5
| to control channel | 4 |  | send to channel | 7
DISM20
| btn | 1-9 | OK
| btn | 10 |  | triggers dism input | 16
| btn | 11 |  | triggers dism input | 17
| btn | 12 |  | triggers dism input | 18
| btn | 13 |  | triggers dism input | 19
| btn | 14 |  | triggers dism input | 20
| btn | 15 |  | triggers dism input | Nothing
| btn | 16 |  | triggers dism input | Nothing
| btn | 17 |  | triggers dism input | Nothing
| btn | 18 |  | triggers dism input | Nothing
| btn | 19 |  | triggers dism input | Nothing
| btn | 20 |  | triggers dism input | Nothing
Dtem01
| problem with rounded value |  |  | See picture
all from same module (dtem01)
as tekst capture used:
$F1
$V
$F2
$F3
Result is always the same with 6 digits after comma